Firmware upgrading SOP

(By UPSReflashTool)

1, Before upgrading the firmware, the UPS should be in Stand-by mode (off-charging) and make sure the battery is connected.

2, Use a RS-232 cable (pin to pin cable) connect the UPS and the Computer

3, Double click  in UPSReflashTool path to run the software

4, Select the COM used by the listbox

5, Click the button  to select the firmware (*.mot or *.s19)

Select the file 36-000678-02s4.mot (burn code provided)，Click button “open”.

6, Click the button  to update the firmware.

Note: before start the firmware upgrading, please check if the com is used by other software. If the process don’t success, please back to step 5 to retry 1~2 time.

The firmware upgrading progress will cost 2~3 minute.

After the firmware upgrading success, the following figure will be show.

Click button “OK” to finish the firmware upgrading.

7, Disconnect AC input and wait until the LCD display is off. The new firmware will be activated when turning on the UPS again.

8, Back to step 5 for other ups.